## Slide 1: BP Center for High Performance Computing Facility – Year One Review
2015 Rice Oil & Gas HPC Workshop
March 4, 2015

## Slide 2
PROJECT TEAM
OWNER: BP
DESIGNER: HOK
CONTRACTOR: ANSLOW BRYANT
COMMISSIONING: ENGINEERED AIR BALANCE (EAB)
PENNINGTON & ASSOCIATES
(Marie D. De Jesús / Houston Chronicle)

## Slide 3
DESIGN
07/11 - 04/12 (9 MO.)
CONSTRUCTION
05/12 - 09/13 (17 MO.)
OPERATION
09/13 - CURRENT (18 MO.)
SCHEDULE

## Slide 4
SUCCESS IN DESIGN, CONSTRUCTION & OPERATION
DELIVERED ON-TIME
WITHIN BUDGET
OPERATING ACCORDING TO OWNER’S REQUIREMENTS
SAFETY
  NO LOST TIME INCIDENTS OR DAYS AWAY FROM WORK
  TIRR TOTAL INCIDENT RATE 2-3x BELOW INDUSTRY AVERAGE
  TRUTHFUL & ACCURATE - MORE THAN 200 INCIDENTS LOGGED
COLLABORATIVE TEAM JOURNEY – BEGINNING TO END
PEER REVIEW – CONTINUOUS PROCESS
  PRE-DESIGN
  DESIGN
  CONSTRUCTION
  COMMISSIONING
  POST OCCUPANCY

## Slide 5
OWNER’S REQUIREMENTS
15 MVA ULTIMATE ELECTRICAL LOAD
TARGET PUE OF 1.35 AVERAGE, 1.5 MAXIMUM
GROWTH CAPABILITY AND FLEXIBILITY (FUTURE-PROOF)
SCALABLE
MAXIMUM 35 KW RACK
REDUNDANCY:
  N + 1 COOLING EQUIPMENT
  2N, 34.5 KV FEEDS FROM CNP
  2N STATIC UPS
PROTECTED WHITE SPACE
HOT AISLE CONTAINMENT

## Slide 6
SITE PLAN
SERVICE DRIVE
BP WAY
GARAGE DRIVE
BUILDING ENTRY
HPC FACILITY
NORTH GARAGE
I-10 SERVICE ROAD
MAINTENANCE PATH
LOADING DOCK

## Slide 7
STACK DIAGRAM
LEVEL 3 – TENANT
LEVEL 2 - TENANT
LEVEL 1 - SUPPORT

## Slide 8
SECTION DIAGRAM
COMPUTING CIRCULATION
COMPUTING / RACK SPACE
COMPUTING SUPPORT
OFFICE
OFFICE SUPPORT
VERTICAL CIRCULATION
ELEVATED SLAB ON GRADE ABOVE 500 YEAR FLOODPLAIN
OVERSIZED SERVICE ELEVATOR
OVERSIZED CORRIDORS
ROBUST ENVELOPE SURROUNDING WHITE SPACE AND SUPPORT SPACE

## Slide 9
ARCHITECTURE AND INTERIOR
VERTICAL CONNECTIVITY
ENTRY APPROACH FROM CAMPUS
ENTRYLOBBY / SECURITY
INTERACTION BP AND CLIENT
PUBLIC PERCERPTION / FREEWAY IMAGE

## Slide 10
ARCHITECTURE AND INTERIOR
VERTICAL CONNECTIVITY
SILICON SPACE
CARBON SPACE / WORK AREAS

## Slide 11
ARCHITECTURE
SECURE, ELEVATED AND COVERED LOADING DOCK
PROTECTED WHITE SPACE WITH PERIMETER PERSONNEL ACCESS
STRUCTURE WITH 300 PSF LOADING
PEOPLE FRIENDLY
PARAPET WALL 5+ FT. ABOVE ROOF
ROOF STRUCTURE SLOPED FOR STRATEGIC DRAINAGE

## Slide 12
COOLING
DISTRIBUTION NETWORK SIZED FOR ULTIMATE LOAD
EQUIPMENT INCREMENTALLY ADDED TO SUPPORT DEMAND
N + 1 EQUIPMENT
DUAL CHILLED WATER SYSTEMS
WATER-COOLED CHILLERS
WATER ECONOMIZER
RESERVE MAKE-UP WATER STORAGE

## Slide 13
LOOP PIPE DISTRIBUTION WITH DUAL FEEDS
PRE-TREATED OUTDOOR AIR SUPPLY
MEASUREMENT AND VERIFICATION (SUBMETERING)
COOLING

## Slide 14
COOLING - WHITE SPACE
CAPABLE OF AIR AND LIQUID COOLING
TREND TOWARDS INCREASED HEAT DENSITY
  INITIALLY 35 KW/RACK
  LATER CHALLENGED (80+ KW/RACK WATER-COOLED)
DEMAND CONTROLLED VAV AIRFLOW IN WHITE SPACE
LIQUID COOLING FOR HIGH HEAT DENSITY APPLICATIONS

## Slide 15
ELECTRICAL
100% REDUNDANCY AT 34.5 KV SERVICE, 5 KV SWITCHGEAR AND SOME 480V / 277V UNIT SUBSTATIONS
BACKUP GENERATORS FOR SOME COMPUTING / RACK SPACE
STATIC UPS ENERGY SAVER MODE
FLYWHEEL TYPE UPS
RACK POWER-BLDG. UTILIZATION VOLTAGE (480V / 3 PHASE)

## Slide 16
ELECTRICAL
MEASUREMENT AND VERIFICATION (SUBMETERING)
HIGH EFFICIENCY TRANSFORMERS
HIGH EFFICIENCY LIGHT SOURCE (LED, T5 & T5HO FLUORESCENT)
AUTOMATED LIGHTING CONTROLS

## Slide 17
OPERATING PERFORMANCE - PUE
Annual Average PUE = 1.32
Chart: Monthly Average PUE
| 41699 | 41730 | 41760 | 41791 | 41821 | 41852 | 41883 | 41913 | 41944 | 41974 | 42005 | 42036
 | 1.3361 | 1.3284 | 1.3132 | 1.3851 | 1.3601 | 1.3501 | 1.3523 | 1.3239 | 1.287 | 1.2652 | 1.2633 | 1.282

## Slide 18
OPERATING PERFORMANCE
SAFE & RELIABLE OPERATIONS
REAL TIME ON-GOING TESTING
PHASED EXPANSION
FLEXIBILITY CHALLENGED
MOVE READY: UP TO 50 RACKS/DAY

## Slide 19
THANK YOU
GARY W. KUZMA PE, CEM, LEED AP, GBE
Director of MEP Engineering
+1 713 407 7739 | gary.kuzma@hok.com
SAADEDDINE DIMACHKIEH PE, CLEP, LEED® AP
Firm Wide Director of Electrical Engineering
+1 713 407 7714 | saad.dimachkieh@hok.com
STEFAN GARRARD
Innovation Lab Project Lead
+1 281 366 3245 | stefan.garrard@bp.com